- 塑料管道系统简介 Plastic piping system

- UPVC/CPVC管道系统 UPVC/CPVC Piping System

- 材料特性 Material Characteristic

PVC是由氯乙烯单体（VCM）聚合而成，PVC材料具有无毒，抗老化及耐酸碱的特性，因此非常适合用于化工管道之使用。而以PVC原料加入一定量的固体添加剂（无增塑剂）组成的混合物，称之为硬质聚氯乙烯（简称UPVC）。Polyvinyl chloride is produced by polymerization of the monomer vinyl chloride (VCM). PVC is used in construction, sewerage pipes and other pipe applications because of its biological and chemical resistance and workability.  It’s more effective than traditional materials such as copper, iron or wood in pipe and profile applications.

CPVC是由聚氯乙烯（PVC）再次氯化改性而成的高分子材料， PVC树脂经过氯化后，氯含量由 56.7% 提高到 63-69%，使化学稳定性增加，从而提高了材料的耐热性、耐酸、碱、盐、氧化剂等的腐蚀；其热变形温度和机械性能均高于UPVC许多。因此， CPVC 是工业管道的最佳工程材料之一。Unplasticised Poly Vinyl Chloride (UPVC) is a rigid form of PVC often used in the building industry as a low-maintenance material.

- 管道系统介绍 Introduction to UPVC/CPVC Piping System

UPVC及CPVC管道系统均具有耐腐蚀、耐冲击、不易变形、内壁光滑、不易结垢、保温性好、不导电、粘接方便、使用寿命长等特性。因此在性价比高与施工费用低廉的优势上逐渐取代其它金属管道系统，而且UPVC及CPVC管道系统维修保养方便快速，无需长时间停机而造成巨大损失，故UPVC及CPVC管道系统是当前工业管道设计的首选。UPVC/CPVC pipes are in widespread use in a number of industries, ranging from residential plumbing to complex water treatment systems. Because of the material properties of UPVC/CPVC pipes, they are highly valuable as a thermo-resistant structure, fire retardant fabric, and as a high quality water conduit in many construction applications. UPVC/CPVC pipes are superior to most other modern materials due to environmental friendliness, chemical resistance, inherent toughness, heat resistance, and being electrically non-conductive/non-corrosive

UPVC管道系统所允许最高使用温度为 60 ℃，长期使用温度为 45 ℃。其适用于输送温度低于45℃的一些腐蚀性介质； 也可以用于普通压力流体的输送，一般用于给排水管道、农业灌溉管道、环境工程管道、空调管道等。Max temperature of UPVC pipes is 60℃, and they are usually used below 45℃.  They are used for water supply system, agriculture irrigation system, and pipes for airconditioning.

CPVC管道系统所允许最高使用温度为 110 ℃，长期使用温度为 95 ℃。其适用于在标准允许的压力范围内输送热水及腐蚀性介质。一般用于石油、化工、电子、电力、冶金、造纸、食品饮料、医药、电镀等工业领域。Max temperature of CPVC pipes is 110℃, and they are usually used below 95℃.  They are used for petro, electronics, chemical engineering, food, and metal plating industries.

- 物理性能 Physical Properties

- UPVC物理性能表 Physical Properties for UPVC

| 项 目 | 单 位 | 标 准 值 | 测 试 方 法 |
| --- | --- | --- | --- |
| 密度 | kg/m³ | 1350～1460 | ISO 1183 |
| 维卡软化温度 | ℃ | （管材）≥80，（配件）≥74 | ISO 2507 |
| 拉伸强度 | MPa | ≥40 | ISO 6259 |
| 冲击强度 | KJ/m² | 11.0 | ISO 179 |
| 纵向回缩率 | % | ≤5 | ISO 2505 |
| 落锤冲击试验（0 ℃） | TIR | ≤10% | ISO 3127 |

| Item | Unit | Standard Value | Standard |
| --- | --- | --- | --- |
| Density | kg/m³ | 1350～1460 | ISO 1183 |
| Vicat | ℃ | Pipes ≥80，Fittings ≥74 | ISO 2507 |
| Tensile Strength | MPa | ≥40 | ISO 6259 |
| Impact Strength | KJ/m² | 11.0 | ISO 179 |
| Vertical Retraction Ratio | % | ≤5 | ISO 2505 |
| Drop-weight Test（0 ℃） | TIR | ≤10% | ISO 3127 |

- CPVC物理性能表 Physical Properties for CPVC

| 项 目 | 单 位 | 标 准 值 | 测 试 方 法 |
| --- | --- | --- | --- |
| 密度 | kg/m³ | 1450～1650 | ISO 1183 |
| 维卡软化温度 | ℃ | （管材）≥110，（配件）≥103 | ISO 2507 |
| 拉伸强度 | MPa | ≥50 | ISO 6259 |
| 冲击强度 | KJ/m² | 8.0 | ISO 179 |
| 纵向回缩率 | % | ≤5 | ISO 2505 |
| 落锤冲击试验（0 ℃） | TIR | ≤10% | ISO 3127 |

| Item | Unit | Standard Value | Standard |
| --- | --- | --- | --- |
| Density | kg/m³ | 1450～1650 | ISO 1183 |
| Vicat | ℃ | Pipes ≥110，Fittings ≥103 | ISO 2507 |
| Tensile Strength | MPa | ≥50 | ISO 6259 |
| Impact Strength | KJ/m² | 8.0 | ISO 179 |
| Vertical Retraction Ratio | % | ≤5 | ISO 2505 |
| Drop-weight Test（0 ℃） | TIR | ≤10% | ISO 3127 |

- UPVC/CPVC管道之使用温度与操作压力对照表 Temp & Pressure relation between UPVC and CPVC pipelines

本表系以常温73℉（23℃）时，UPVC/CPVC管道之使用操作压力为100%，随着温度的升高，其操作压力残余的百分比。

The operating pressure  in the UPVC and CPVC pipelines at higher temperatures is listed  in the following table, with the pressure at the at normal operating temperature 23℃  scaled to be 100%

| ℉ | 73 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ℃ | 23 | 27 | 32 | 38 | 43 | 49 | 54 | 60 | 66 | 71 | 77 | 82 | 88 | 93 | 99 |
| UPVC | 100% | 90% | 75% | 62% | 50% | 40% | 30% | 22% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |
| CPVC | 100% | 100% | 91% | 82% | 73% | 65% | 57% | 50% | 45% | 40% | 32% | 25% | 22% | 20% | 0% |

PS：有带螺牙的管线，UPVC部分不得超过110℉（43℃）；CPVC部分不得超过150℉（66℃）。

Note: UPVC pipes with screws should not be operated over 110 ℉(43℃); CPVC ones should not be operated over 150℉（66℃）

- PPR/PPH管道系统 PPR/PPH Piping System

- 材料特性 Material Characteristics

PP-R则是由丙烯单体Propylene和乙烯单体Ethene聚合而成的共聚物（Poly Propylene Copolymer），采用先进的气相共聚工艺，PE在PP的分子链中随机、均匀地进行聚合，这种原料称之PP-R(无规共聚聚丙烯）；Polypropylene (PP), also known as polypropene, is a thermoplastic polymer used in a wide variety of applications including packaging and labeling, textiles (e.g., ropes, thermal underwear and carpets), stationery, plastic parts and reusable containers of various types, laboratory equipment, loudspeakers, automotive components, and polymer banknotes.

There are three general types of polypropylene: homopolymer, random copolymer, and block copolymer. The comonomer is typically used with ethylene.

Polypropylene Random Copolymer (PP-R) is formulated by adding randomly polymerized ethylene monomer to polypropylene homopolymer.  It decreases the polymer crystallinity and makes the polymer more transparent.

PP-H就是由丙烯单体Propylene聚合而成的均聚物，它经过β改性具有细腻的结晶结构，使其具有比PPR更优良的耐化学性、耐高温性以及良好的抗蠕变性，而且在低温下还具有优异的抗冲击性。因此，更适合使用在工业管道系统中。Polypropylene Homopolymer (PP-H) is another type of PP. It has better temperature & creep resistance than PPR, and with low temperature impact strength.

- 管道系统介绍 Introduction to PPR/PPH Piping System

PPR及PPH管道系统均具有可挠性、耐腐蚀、耐冲击、内壁光滑、不易结垢、保温性好、不导电、无毒性、质量轻等特性。 Presently PPH/PPR pipes & fittings are most reliable in plumbing and water supply plants, due to their chemical features and fusion welding, which ensures the plumbing to have a perfect seal tight system.

Approved by the Health Organization, Eco-Friendly Quality, Temperature Resistance Quality etc, puts PPH/PPR pipes & fittings as the best selection.

PPR管道系统所允许最高使用温度为95 ℃，长期使用温度为 70 ℃。其适用于输送温度低于70℃的某些腐蚀性介质； 也可以用于普通压力冷热流体的输送，一般用于民用建筑物内的冷热水管道系统等。Max temperature of PPR pipes is 95℃, and they are usually used below 70℃.  They are used for transferring corrosive material below 70℃, and also for pressured liquid transfer, for example, household water system.

PPH管道系统所允许最高使用温度为110℃，长期使用温度为90 ℃。主要用在工业管道系统中，其适用于工艺冷却水和化工行业的耐腐蚀性介质输送，同时也广泛应用于钢厂（酸洗、酸再生、酸雾）、烟气脱硫、离子膜烧碱等管道系统中。Max temperature of PPH pipes is 110℃, and they are usually used below 90℃.  They are used for cooling water transfer, corrosive material transfer, fume ducts, electrolyze systems, and other piping systems with acid liquids.

- 物理性能 Physical Properties

- PPR物理性能表 Physical Properties of PPR Pipes

| 项 目 | 单 位 | 标 准 值 | 测 试 方 法 |
| --- | --- | --- | --- |
| 密度 | kg/m³ | 900～920 | ISO 1183 |
| 维卡软化温度 | ℃ | ≥91 | ISO 2507 |
| 拉伸强度 | MPa | ≥25 | ISO 6259 |
| 冲击强度（23 ℃） | KJ/m² | 40 | ISO 179 |
| 纵向回缩率(135 ℃) | % | ≤2 | ISO 2505 |

| Item | Unit | Standard Value | Standard |
| --- | --- | --- | --- |
| Density | kg/m³ | 900～920 | ISO 1183 |
| Vicat | ℃ | ≥91 | ISO 2507 |
| Tensile Strength | MPa | ≥25 | ISO 6259 |
| Impact Strength（23 ℃） | KJ/m² | 40 | ISO 179 |
| Vertical Retraction Ratio (135 ℃) | % | ≤2 | ISO 2505 |

- PPH物理性能表Physical Properties of PPH Pipes

| 项 目 | 单 位 | 标 准 值 | 测 试 方 法 |
| --- | --- | --- | --- |
| 密度 | kg/m³ | 905～915 | ISO 1183 |
| 维卡软化温度 | ℃ | ≥95 | ISO 2507 |
| 拉伸强度 | MPa | ≥27 | ISO 6259 |
| 冲击强度（23 ℃） | KJ/m² | 50 | ISO 179 |
| 纵向回缩率(150 ℃) | % | ≤2 | ISO 2505 |

- 塑料管道粘接方法及水压试验注意事项Plastic pipiing system constructing method & Hydrostatic Pressure Testing Notification

- UPVC/CPVC管道粘接方法  Constructing Method of UPVC/CPVC Pipes

UPVC/CPVC管道系统是以专用胶合剂来粘接，具体步骤如下：

UPVC/CPVC piping systems are bonded by special solvent. Hereunder are the steps:

- 切管 Cutting

切管可以用电锯、管道剪刀或塑胶管道切割器，在切割时要确保管口垂直平整，使管在粘合时有较大的粘合面。

Power Saw and plastic tubing cutters can be used for pipe cutting. Cut the pipes as squarely as possible to provide maximum bonding area.

- 打磨 Deburring

利用去角工具、锉刀或砂纸将管切口内外的毛边和锉屑清除干净，使管和配件在粘合时可紧密结合。

Burrs must be removed from the inside, as well as the outside, of the pipe ends by pliers, filer and sandpaper on both inner side and outside of the cutting edge so that pipes and fittings are bond tightly.

- 标线 Marking

在连接之前，要在每支管道外做好承插深度标记，防止在连接时未将管道插配件底部，造成连接处漏水。

Making marks on all pipes according to the length & depth of fitting parts. It can be used to ensure the pipe is completely bottomed into the fitting during assembly.

- 涂抹胶合剂 Solvent Coating

管和配件连接的粘合面需先用清洁剂来渗透软化，以增加溶剂粘胶之溶接效果，使用破布将溶剂均匀的涂抹在管材插口的外面和管件承口的内表面。

溶接剂标准用量Standard Volume of Cement

| Nominal Outside Diameter（mm） | 20 | 25 | 32 | 40 | 50 | 63 | 75 | 90 | 110 | 125 | 140 | 160 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Cement Volume（g/piece） | 0.40 | 0.58 | 0.88 | 1.31 | 1.94 | 2.97 | 4.10 | 5.73 | 8.43 | 10.75 | 13.37 | 17.28 |

- 连接 Assembling

涂完沾剂后，应立即将管插入配件套接并旋转1/4圈，管必须插入配件底部，结合时应维持10-15秒固定确保初步接合，（6″以上管件之结合，需要2人合作完成），管和管件接合点的周围胶水溢出应很明显，如果套接口周围溢出的胶水不连续，表示所涂的胶水不足，如果过量溢出，要用布擦去，胶水不少涂抹亦不可涂抹过多。

After coating cement, insert pipe into fitting socket while rotate the pipe a quarter turn. Pipe must bottom completely to the fitting stop. Hold the assembly for 10-15 seconds to ensure initial bonding (2 persons work together to bond pipes larger than 6”). A bead of cement should be evident around the pipe and fitting juncture. If this bead is not continuous around the socket shoulder, it may indicate that insufficient cement was applied. If insufficient cement is applied, the joint must be cut out, discarded and begun again. Cement in excess of the bead can be wiped of with a rag.

- UPVC/CPVC管道系统水压试验注意事项Hydrostatic Pressure Testing Notification of UPVC/CVPC Pipes

- 对于粘接连接的管道必须在安装48小时后才能进行试压。管道的强度试压要在沟槽回填达到要求后才能进行。

Cemented pipes must be tested 48 hours after installation. If pipes are installed underground, the test must be done after the trench is backfilled.

- 试压管段上的三通、弯头特别是管道末端的管堵的支撑要有足够的稳定性，若采用混凝土结构的止推块，试验前要有充分的凝固时间，使其达到规定的抗压强度。

Support to tees, elbows, and fitting stops in the end must be stable. Thrust block made of concrete must be cured completely before test.

- 将试压管道末端封堵，缓慢注水，同时将管道内气体排出。

The end of the system should be blocked. Then, the system must be filled slowly with water, venting air from valves at piping run ends and at elevations during the filling process.

- 充满水后，进行水密检查。

After the system is filled with water, make watertight test.

- 加压宜用手动泵或电动泵缓慢加压，升压时间不得小于10min.

Hand pump or electro pump is used to rise up the pressure. The process must be slowly, more than 10 mins.

- 升至规定试验压力后，停止加压，稳压1h，观察接头部位是否有漏水现象。若出现降压时，补压至规定试验压力值，15 min内的压力降不超过0.05MPa为合格。

After rising up to the test pressure, hold it for 1 hour to check if there is leakage. If the pressure lowers down, rise up the pressure again. Within 15mins, if the pressure lowers smaller than 0.05MPA, the result is qualified.

- PPR/PPH管道粘接方法 Constructing Method of UPVC/CPVC Pipes

PPR/PPH管道系统是以热熔接的方式粘接，具体步骤如下：

PPR/PPH piping systems are bonded by heating. Hereunder are the steps:

- 切管 Cutting & Deburring

管道设计要求将管切断，在切割时要确保管口垂直平整、清洁、无油，要用锉刀或砂纸将管切口内外的毛边和锉屑清除干净。

Power Saw and plastic tubing cutters can be used for pipe cutting. Cut the pipes as squarely as possible to provide maximum bonding area and keep it clean without oil. Burrs must be removed from the inside, as well as the outside, of the pipe ends by pliers, filer and sandpaper on both inner side and outside of the cutting edge so that pipes and fittings are bond tightly.

- 标线 Marking

在连接之前，要在每支管道外做好承插深度标记，防止在连接时未将管道插配件底部，造成连接处漏水。

Making marks on all pipes according to the length & depth of fitting parts. It can be used to ensure the pipe is completely bottomed into the fitting during assembly.

- 加热 Heating

管材应无旋转地将管端导入加热套内，插人到所标志的连接深度，同时，无旋转地把管件推到加热头上，并达到规定深度标志处。

Guide the pipes into heater straight to the marked assembly depth. In the meanwhile, push the fitting onto the heater and reach the marked depth.

- 连接 Assembly

加热时间必须符合下表的规定。达到规定的加热时间后，必须立即将管材与管件从加热套和加热头上同时取下，迅速无旋转地直线均匀地插入到所标深度，使接头处形成均匀的凸缘，在规定的加工时间内，刚熔接好的接头允许立即校正，但严禁旋转。应固定好管材、管件，使它不受扭、受弯和受拉。

Heating time must be complied with the values in the under table. After heating time, remove pipe and fitting from the heater immediately and assemble them to the marked depth straight so that there is even bulge is the assembly place. Within the working time, tiny adjustment can be made but rotation must be prohibited. Keeping pipe and fitting from being wrenched, bent, and stretched.

| 公称管材（mm） | 热熔深度(mm) | 加热时间(s) | 熔接时间(s) | 冷却时间（min） |
| --- | --- | --- | --- | --- |
| 20 | 14.0 | 5 | 4 | 2 |
| 25 | 15.0 | 7 | 4 | 2 |
| 32 | 16.5 | 8 | 6 | 4 |
| 40 | 18.0 | 12 | 6 | 4 |
| 50 | 20.0 | 18 | 6 | 4 |
| 63 | 24.0 | 24 | 8 | 6 |
| 75 | 26.0 | 30 | 8 | 8 |
| 90 | 29.0 | 40 | 8 | 8 |
| 110 | 32.5 | 50 | 10 | 8 |

若环境温度低于5℃，加热时间延长50%

| Nominal Diameter（mm） | Heating Depth (mm) | Heating Time (s) | Assembly Time (s) | Cooling Time（min） |
| --- | --- | --- | --- | --- |
| 20 | 14.0 | 5 | 4 | 2 |
| 25 | 15.0 | 7 | 4 | 2 |
| 32 | 16.5 | 8 | 6 | 4 |
| 40 | 18.0 | 12 | 6 | 4 |
| 50 | 20.0 | 18 | 6 | 4 |
| 63 | 24.0 | 24 | 8 | 6 |
| 75 | 26.0 | 30 | 8 | 8 |
| 90 | 29.0 | 40 | 8 | 8 |
| 110 | 32.5 | 50 | 10 | 8 |

If the environment temperature is lower than 5℃, heating time must be 50% longer.

- PPR/PPH水压试验注意事项 Hydrostatic Pressure Testing Notification of PPR/PPH Pipes

- 水压试验宜分段进行，试验管段的总长度不宜超过500m；

- 试验前，管道应固定，接头需明放，且不得连接配水器具；

- 压力表安装在试验管段的最低处，压力精度为0.01Mpa；

- 从管段最低处缓缓地向管道内充水，充分排除管道内的空气，进行水密性试验；

- 对管道缓缓升压，升压宜用手动泵，升压时间不小于10min；

- 升压至规定的试验压力后，稳压1小时，压力降不得超过0.06Mpa；

- 在工作压力的1.15倍状态下，稳压2小时，压力降不得超过0.03Mpa；

- 试验过程中，各连接处不得有渗漏现象；

- 在30分钟内允许两次补压，升至规定试验压力。

- Hydraulic test has to be performed sectional; tested length should be no longer than 500m.

- Before test, make sure pipes are fixed, joints are not covered, and the whole system is independent from water outlet tools.

- Pressure gage with tolerance 0.01Mpa needs to be installed in the lowest place of the system.

- Fill water from lowest part of the system to remove the air and make watertight test.

- Hand pump or electro pump is used to rise up the pressure. The process must be slowly, more than 10 mins.

- After rising up to the test pressure, hold it for 1 hour to check if there is leakage. If the pressure lowers smaller than 0.06MPA, the result is qualified.

- Hold the pressure 1.15 times of the working pressure for 2 hours. If the pressure lowers smaller than 0.03MPA, the result is qualified.

- There must be no leakage in the system during test.

- During 30 mins, if the pressure lowers down, it is allowed to raise up the pressure again 2 times.

- 塑料管道的最大支承间距规定Max Support Distance Requirement

由于塑胶管道的刚性不如钢管等金属管道，故在其室内管道的安装中对最大支承间距有着严格的要求：若管道布置环境可能令管道的温度较高时，应缩短管道工支承的间距，请参考下表数值：

Support distance of plastic pipes is more strictly requested than that of steel pipe. Operating temperature influence the distance. Please refer to the below charts:

- UPVC管道支承最大间距（mm）UPVC Support Spacing Chart

| 标准尺寸 | 1/2″ | 3/4″ | 1″ | 1-1/4″ | 1-1/2″ | 2″ | 2-1/2″ | 3″ | 4″ | 6″ | 8″ |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 横管 | 500 | 550 | 650 | 800 | 950 | 1100 | 1200 | 1350 | 1550 | 1800 | 2400 |
| 立管 | 900 | 1000 | 1200 | 1400 | 1600 | 1800 | 2000 | 2200 | 2400 | 2700 | 3000 |

| Nominal Pipe Size | 1/2″ | 3/4″ | 1″ | 1-1/4″ | 1-1/2″ | 2″ | 2-1/2″ | 3″ | 4″ | 6″ | 8″ |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Horizontal Pipes | 500 | 550 | 650 | 800 | 950 | 1100 | 1200 | 1350 | 1550 | 1800 | 2400 |
| Vertical Pipes | 900 | 1000 | 1200 | 1400 | 1600 | 1800 | 2000 | 2200 | 2400 | 2700 | 3000 |

- CPVC管道支承最大间距（mm）CPVC Support Spacing Chart

| 管径 | 1/2″ | 3/4″ | 1″ | 1-1/4″ | 1-1/2″ | 2″ | 2-1/2″ | 3″ | 4″ | 6″ | 8″ |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 20℃ | 700 | 750 | 800 | 850 | 1000 | 1100 | 1250 | 1400 | 1650 | 1800 | 2000 |
| 40℃ | 650 | 700 | 750 | 800 | 950 | 1050 | 1200 | 1350 | 1500 | 1650 | 1800 |
| 60℃ | 600 | 650 | 700 | 750 | 900 | 1000 | 1100 | 1250 | 1350 | 1500 | 1650 |
| 80℃ | 550 | 600 | 650 | 700 | 800 | 900 | 1000 | 1100 | 1200 | 1350 | 1500 |
| 立管 | 1000 | 1100 | 1200 | 1400 | 1600 | 1800 | 2100 | 2400 | 2700 | 3000 | 3400 |

| Nominal Pipe Size | 1/2″ | 3/4″ | 1″ | 1-1/4″ | 1-1/2″ | 2″ | 2-1/2″ | 3″ | 4″ | 6″ | 8″ |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 20℃ | 700 | 750 | 800 | 850 | 1000 | 1100 | 1250 | 1400 | 1650 | 1800 | 2000 |
| 40℃ | 650 | 700 | 750 | 800 | 950 | 1050 | 1200 | 1350 | 1500 | 1650 | 1800 |
| 60℃ | 600 | 650 | 700 | 750 | 900 | 1000 | 1100 | 1250 | 1350 | 1500 | 1650 |
| 80℃ | 550 | 600 | 650 | 700 | 800 | 900 | 1000 | 1100 | 1200 | 1350 | 1500 |
| Vertical Pipes | 1000 | 1100 | 1200 | 1400 | 1600 | 1800 | 2100 | 2400 | 2700 | 3000 | 3400 |

- PPR/PPH管道支承最大间距（mm）PPR/PPH Support Spacing Chart

- 冷水管支之吊架最大间距 Max distance for cold water pipes

| 标准尺寸 | 20 | 25 | 32 | 40 | 50 | 63 | 75 | 90 | 110 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 横管 | 650 | 800 | 950 | 1100 | 1250 | 1400 | 1500 | 1600 | 1900 |
| 立管 | 1000 | 1200 | 1500 | 1700 | 1800 | 2000 | 2000 | 2100 | 2500 |

| Nominal Diameter | 20 | 25 | 32 | 40 | 50 | 63 | 75 | 90 | 110 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Horizontal pipes | 650 | 800 | 950 | 1100 | 1250 | 1400 | 1500 | 1600 | 1900 |
| Vertical pipes | 1000 | 1200 | 1500 | 1700 | 1800 | 2000 | 2000 | 2100 | 2500 |

- 热水管支之吊架最大间距Max distance for hot water pipes

| 标准尺寸 | 20 | 25 | 32 | 40 | 50 | 63 | 75 | 90 | 110 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 横管 | 500 | 600 | 700 | 800 | 900 | 1000 | 1100 | 1200 | 1500 |
| 立管 | 900 | 1000 | 1200 | 1400 | 1600 | 1700 | 1700 | 1800 | 2000 |

| Nominal Diameter | 20 | 25 | 32 | 40 | 50 | 63 | 75 | 90 | 110 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Horizontal pipes | 500 | 600 | 700 | 800 | 900 | 1000 | 1100 | 1200 | 1500 |
| Vertical pipes | 900 | 1000 | 1200 | 1400 | 1600 | 1700 | 1700 | 1800 | 2000 |

- 管道与构筑物及其它管道的间距 Spacing among water supply system, non-building structures, and other pipelines

|  | 构筑物 |  |  |  | 其它管道 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 铁路 | 建筑红线 | 街树中心 | 电杆 | 电缆 | 煤气管 | 热力管 | 污水管 |
| 最小间距（M） | 5 | 5 | 1.5 | 1.0 | 1.0 | 1.0-2.0 | 1.5 | 1.5 |

|  | Nonbuilding Structures |  |  |  | Other Pipelines |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Railway | Building Line | Street Trees | Poles | Electric Wires | Gas Pipelines | Heating Pipelines | Sewage Pipelines |
| Min. Space （M） | 5 | 5 | 1.5 | 1.0 | 1.0 | 1.0-2.0 | 1.5 | 1.5 |